附件4

Discharge Standard of Water Pollutants for Rural Domestic Sewage Treatment Facilities

Abstract：

1. This document specifies the control, monitoring, and supervision requirements for water pollutant discharge from rural domestic sewage treatment facilities with a design capacity under 300 m3/d in Shanghai.

2. The effluent from rural domestic sewage treatment facilities with a design capacity <5 m3/d must visually be free from blackening and odor. If blackening and odor are observed, the effluent shall comply with the Grade III Standard.

3. Facilities with a design capacity ≥100 m3/d, whose effluent is discharged into water bodies classified as Class III environmental functional zones or higher according to GB 3838, shall comply with the Grade I Standard.

4. Facilities with a design capacity ≥5 m3/d and <100 m3/d, whose effluent is discharged into water bodies classified as Class Ⅲ environmental functional zones or higher according to GB 3838, shall comply with the Grade Ⅱ Standard.

5. Facilities with a design capacity ≥5 m3/d and <300 m3/d, whose effluent is discharged into water bodies of other environmental functional zones or with undefined environmental functions (such as ponds near villages), shall comply with the Grade III Standard.

6. The permissible discharge limits for the effluent from rural domestic sewage treatment facilities are shown as below:

| No. | Item | Grade Ⅰ standard | Grade Ⅱ standard | Grade Ⅲ standard |
| --- | --- | --- | --- | --- |
| 1 | pH | 6～9 |  |  |
| 2 | CODCr, mg/L | 50 | 60 | 80 |
| 3 | SS, mg/L | 20 | 30 | 30 |
| 4 | NH3-N, mg/L | 8（15）a | 20 | 20 |
| 5 | TN, mg/L | 20 | 25b | 25b |
| 6 | TP, mg/L | 1 | 2 | 3（2）c |
| 7 | Animal and Vegetable Oils, mg/Ld | 3 | 3 | 5 |
| a. These limits in parentheses shall be applied from November 1 to March 31 of the following year. b. These limits shall be applied when the effluent is discharged into enclosed water bodies (including ponds, dead-end river segments, etc.) or into non-compliant water bodies where the exceeding parameter is nitrogen. c. These limits in parentheses shall be applied when the effluent is discharged into enclosed water bodies (including ponds, dead-end river segments, etc.) or into non-compliant water bodies where the exceeding parameter is phosphorus. d. These limits shall be applied to treatment facilities receiving rural tourism sewage. |  |  |  |  |